## DGA Report
DELHI TRANSCO LTD. (Regd. Office: Shakti Sadan, Com. Inderjeet Gupta Road, New Delhi-110002) CENTRALISED TESTING LAB 220 KV GIS SUB STN MAHARANI BAGH, Behlolpur Khadar Opp ISBT Sarai Kale Khan, NEW Delhi –13
Dissolved Gas Analysis Lab Testing Report Report ID: AN-2026-0316
Name Plate Data |  |  | Sample Data:
Name of S/S: Subzi Mandi Equipment ID: 2 Make: EMCO Serial Number: HT1644/12427 Vector Group: N/A Equipment Rating: 100 MVA, 220/33 kV Yr. of Manufacturing: N/A Yr. of Commissioning: 2005-07-01 |  |  | Date of Sampling: 2025-05-31 Sample Received: 2025-05-31 Type of Equipment: N/A Sampling Point: N/A
Additional Information
Load at the time of Sampling (MW/Amps): N/A Winding Temperature (HV/LV/TV): N/A Oil Temperature: N/A Date of Last Filtration: N/A
Reason for Testing: N/A If forced, reason thereof: N/A |  |  | Test Date: 2025-05-31
Violation / Max. Limits in ppm (As per IEEE Std C57.104-2019)
PARAMETERS | O2/N2 not measured (defaults to > 0.2 table)
Transformer Age in Years
| Table-1 (90P) |  | Table-2 (95P) |  |  | Table-3 (Delta) | Table-4 (95P Rate)
| 1-9 yr | 10-30 yr | 1-9 yr | 10-30 yr | >30 yr |  | 4-9 mo | 10-24 mo
Hydrogen H2 | 40 | 40 | 90 | 90 | 90 | 25 | 25 | 10
Carbon Di-oxide CO2 | 3500 | 5500 | 5000 | 8000 | 8000 | 1750 | 1000 | 800
Carbon Mono-oxide CO | 500 | 500 | 600 | 600 | 600 | 175 | 100 | 80
Ethylene C2H4 | 25 | 60 | 80 | 125 | 125 | 20 | 7 | 5
Ethane C2H6 | 15 | 15 | 30 | 40 | 40 | 7 | 3 | 2
Methane CH4 | 20 | 20 | 60 | 60 | 30 | 10 | 4 | 3
Acetylene C2H2 | 2 | 2 | 7 | 7 | 7 | ANY | ANY | ANY
Dissolved Gas Results (in ppm) |  |  | DGA Diagnostics
Parameter | Ist-Prior | Present | DGA Interpretation as per IEEE Std. C57.104-2019
| 2025-05-28 | 2025-05-31
Hydrogen H2 | 76 | 71 | DGA Violation |  |  |  | Yes
Carbon Di-oxide CO2 | 4594 | 4839 | DGA Status |  |  |  | Investigate
Carbon Mono-oxide CO | 594 | 579 | CO2/CO Ratio |  |  |  | 8.36
Ethylene C2H4 | 2007 | 1945 | Rogers Ratio Method |  |  |  | N/A
Ethane C2H6 | 324 | 281 | Duval Triangle Method |  |  |  | T3 (refined: T3)
Methane CH4 | 684 | 683 | Water Content (ppm) mg/kg |  |  |  | N/A
Acetylene C2H2 | 2.5 | 3 | Tan Delta (%) |  |  |  | N/A
TDCG | 3687.5 | 3562 | Resistivity (Giga Ohm-M) |  |  |  | N/A
Sampling Interval: N/A
Asstt. Manager(T) CTL | [6 empty] | Manager(T) CTL