| . |  | DELHI TRANSCO LTD. (Regd. Office: Shakti Sadan, Com. Inderjeet Gupta Road, New Delhi-110002) CENTRALISED TESTING LAB 220 KV GIS SUB STN MAHARANI BAGH, Behlolpur Khadar Opp ISBT Sarai Kale Khan, NEW Delhi –13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dissolved Gas Analysis Lab. Testing Report Report ID: DGA/MHB/2026-27/2026/05/27/0075 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name Plate Data |  |  |  |  |  | Sample Data: |  |  |  |  |  |  |  |  |  |  |
| Name of S/S: 220kV Shalimar Bagh Equipment ID: 100 MVA-I (New) Make: BHEL Serial Number: 2062073 Vector Group: YNyn0d11 Equipment Rating: 100 MVA, 220/33/11 kV Yr. of Manufacturing: 2026 Yr. of Commissioning: 07.05.2026 |  |  |  |  |  | Date of Sampling: 27.05.2026 Sample Received: 27.05.2026 Type of Equipment: Main Tank Sampling Point: Bottom |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Additional Information |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Load at the time of Sampling (MW/Amps): 38MW Winding Temperature (HV/LV/TV): 52°C/52°C /48°C Oil Temperature: 54°C Date of Last Filtration: 07.05.2026 (New oil) |  |  |  |  |  |  |  |  |  |  |
| Reason for Testing: Scheduled Test Date: 27.05.2026 If forced, reason there of: After 2 WEEKS of load taken. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Violation/Max. Limits in ppm (As per IEEE Std C57.104-2019) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PARAMETERS | O2/N2Ratio>0.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Transformer Age in Years |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Table-1(90P) |  |  |  | Table-2(95P) |  |  |  |  |  |  | Table-3 (DELTA) |  | Table-4(95P) |  |  |
|  | 1-9 |  |  | 10-30 | 1-9 |  |  |  | 10-30 |  | >30 |  |  | 4-9 Months | 10-24 Months |  |
| Hydrogen H2 | 40 |  |  | 40 | 90 |  |  | 90 |  | 90 |  | 25 |  | 25 |  | 10 |
| Carbon Di-oxide CO2 | 3500 |  |  | 5500 | 5000 |  |  | 8000 |  | 8000 |  | 1750 |  | 1000 |  | 800 |
| Carbon Mono-oxide CO | 500 |  |  | 500 | 600 |  |  | 600 |  | 600 |  | 175 |  | 100 |  | 80 |
| Ethylene C2H4 | 25 |  |  | 60 | 80 |  |  | 125 |  | 125 |  | 20 |  | 7 |  | 5 |
| Ethane C2H6 | 15 |  |  | 15 | 30 |  |  | 40 |  | 40 |  | 7 |  | 3 |  | 2 |
| Methane CH4 | 20 |  |  | 20 | 60 |  |  | 30 |  | 30 |  | 10 |  | 4 |  | 3 |
| Acetylene C2H2 | 2 |  |  | 2 | 7 |  |  | 7 |  | 7 |  | ANY |  | ANY |  | ANY |
| DISSOLVED GAS RESULTS: (in ppm): |  |  |  |  |  |  | DISSOLVED GAS DIAGNOSTICS: |  |  |  |  |  |  |  |  |  |
| PARAMETERS | Ist-Prior |  | Present |  |  |  | DGA Interpretation as per IEEE Std. C57.104-2019: |  |  |  |  |  |  |  |  |  |
|  | 12.05.26 |  | 27.05.26 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrogen H2 | <5 |  | <5 |  |  |  | DGA Violation |  |  |  |  |  | -- |  |  |  |
| Carbon Di-oxide CO2 | 254 |  | 299 |  |  |  | DGA Status |  |  |  |  |  | -- |  |  |  |
| Carbon Mono-oxide CO | 25 |  | 38 |  |  |  | CO2/CO Ratio |  |  |  |  |  | 7.89 |  |  |  |
| Ethylene C2H4 | 15 |  | <1 |  |  |  | Rogers Ratio Method |  |  |  |  |  | No Diagnosis available |  |  |  |
| Ethane C2H6 | 8 |  | <1 |  |  |  | Duval Triangle Method |  |  |  |  |  | -- |  |  |  |
| Methane CH4 | 13 |  | 1 |  |  |  | Water Content (ppm) mg/kg |  |  |  |  |  | -- |  |  |  |
| Acetylene C2H2 | <0.5 |  | <0.5 |  |  |  | Tan Delta (%) |  |  |  |  |  | 0.4 |  |  |  |
| TDCG | 65 |  | 43 |  |  |  | Resistivity (Giga Ohm-M) |  |  |  |  |  | 246 |  |  |  |
| Sampling Interval: 1 Month |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Asstt. Manager(T)CTL

Manager(T)CTL